{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Sheet1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":110,"n_cols":17,"rows_kept":110,"cut":false,"hidden":false,"merged":[]}
["id","parentStepName","stepMark","stepName","stepDescr","stepMattersNeedingAttention","stepVideoNames","stepPictureNames","toolName","audioClipName","position","rotation","en_parentStepName","en_stepName","en_stepDescr","en_stepMattersNeedingAttention","guid"]
["1","安装前检查准备","安装前检查准备-1-确认安装方案","确认安装方案","结合现场实际情况，基础检查，质量标准，工作范围及安全注意事项，确认安装方案","","","","","1","0/4.04/15","0/180/0","","","","","c15b334b-3f5f-4b83-bea1-f54a0deeba67"]
["2","安装前检查准备","安装前检查准备-2-工作票的办理","工作票的办理","办理工作票，工作许可，确认工作班成员","","","","","2","0/4.04/15","0/180/0","","","","","80f46f3f-5df4-4a24-b7a3-b89608e4ce97"]
["3","安装前检查准备","安装前检查准备-3-安全及交底","安全及交底","对工作班成员技术交底","","","","","3","-1.531914/3.445328/13.1477","20.45002/198.9002/4.556E-07","","","","","a198eafc-b0f2-4790-a350-392b21137d64"]
["4","安装前检查准备","安装前检查准备-4-工器具和备品的准备","工器具和备品的准备","准备工器具及耗材备品","","","","","4","0.3155372/7.629141/17.96508","13.25003/180.7498/4.522667E-07","","","","","e356315b-b985-4df1-8316-d42ba6d557ab"]
["5","现场安全隔离与布置","现场安全隔离与布置-5-工作区域设置隔离","工作区域设置隔离","设置工作区域，隔离带，防止无关人员进入，带电区域工作时，与带电设备保持足够的安全距离","","","","安全围栏","5","4.509541/5.027296/19.56","18.10003/194.0499/4.491109E-07","","","","","0884dc70-a72a-4433-8985-bc5b3fa6c389"]
["6","现场安全隔离与布置","现场安全隔离与布置-6-悬挂警示牌","悬挂警示牌","在隔离带上悬挂相应的警示标牌","","","","“从此处进”标识牌","6","5.713955/1.433328/15.53113","10.30003/176.5499/4.881137E-07","","","","","f6a440ae-0a9b-4368-91f8-c9a8580066a3"]
["7","现场安全隔离与布置","现场安全隔离与布置-7-断开电源开关","断开电源开关","断开将发电机定转子的电源开关","","","","","7","4.807621/4.992635/13.20239","11.70003/202.8/4.359445E-07","","","","","44e038d3-1d4b-41e7-a407-e7069d2083d1"]
["8","现场安全隔离与布置","现场安全隔离与布置-8-执行安全锁定","执行安全锁定","确保主控已切换至维护模式，塔底与机舱上锁挂牌已完成","必须双重验证断电与刹车状态，防止意外启动。","","","","8","4.807621/4.992635/13.20239","11.70003/202.8/4.359445E-07","","","","","808abeca-8b89-42ce-ae29-3f6566a5ed36"]
["9","现场安全隔离与布置","现场安全隔离与布置-9-临时物品存放区域设置","临时物品存放区域设置","铺设防潮布，用于摆放工具及拆卸元件，规范管理，禁止物品落地","","","","防潮布","9","-0.08678801/3.114869/12.67531","33.65007/179.2501/5.128155E-07","","","","","d378ffe4-d3cd-43b5-8cdc-d8c3678b10bf"]
["10","现场安全隔离与布置","现场安全隔离与布置-10-工作电源准备","工作电源准备","准备充足的电源及小型电动工具试验设备","","","","电源盘","10","-0.08678801/3.114869/12.67531","33.65007/179.2501/5.448666E-07","","","","","1d6585af-23b8-4402-84bd-d797ff6f6e0b"]
["11","拆卸齿箱连接器","拆卸齿箱连接器-11-机舱内部准备与清理","机舱内部准备与清理","机舱罩板已移除，作业区域已清理，妨碍物已标记并拆除。现场整洁，具备作业条件。","防止高空坠物。","","","","11","","","","","","","9905f177-09fd-4e3f-900f-beedf6159c67"]
["12","拆卸齿箱连接器","拆卸齿箱连接器-12-打开机舱后吊孔盖","打开机舱后吊孔盖","打开机舱后吊孔盖","","","","","12","-1.145076/115.0712/2.932633","324/231.6993/1.055321E-05","","","","","df205a57-01ec-4cff-93f3-a46c04d336c6"]
["13","拆卸齿箱连接器","拆卸齿箱连接器-13-打开机舱盖螺栓","打开机舱盖螺栓","打开机舱盖螺栓","","","","","13","-1.145076/115.0712/2.932633","324/231.6993/1.055321E-05","","","","","35b1d37a-8fb6-41c1-8e13-0ede2dfa3f8d"]
["14","拆卸齿箱连接器","拆卸齿箱连接器-14-打开吊孔口","打开吊孔口","打开吊孔口","工作人员系好安全防护","","","","14","-1.145076/115.0712/2.932633","324/231.6993/1.055321E-05","","","","","b5e9a2da-7b79-4b86-bc45-b04c5269092c"]
["15","拆卸齿箱连接器","拆卸齿箱连接器-15-用风塔顶吊葫芦吊装工具","用风塔顶吊葫芦吊装工具","使用风塔顶吊葫芦起吊检修部件及工器具，吊至机舱，将地面的工器具升至机舱","防止高空坠物，防止人员跌落","","","","15","-4.095811/121.6584/0.5883147","24.34564/279.4837/0.002035393","","","","","9beaa2b1-badb-4304-9370-3c729b57ab85"]
["16","拆卸齿箱连接器","拆卸齿箱连接器-16-关闭润滑油供油装置","关闭润滑油供油装置","关闭润滑油供油装置","","","","","16","-4.299868/121.5979/-2.170645","48.55006/0.000228584/1.026794E-05","","","","","2413c302-16c9-4e8d-9305-9a45a07336ce"]
["17","拆卸齿箱连接器","拆卸齿箱连接器-17-拆除发电机与齿箱连接器保护罩","拆除发电机与齿箱连接器保护罩","使用开口扳手拆除发电机与齿箱连接器保护罩","","","","开口扳手","17","-3.220337/121.5931/-1.652164","49.30006/0.6001925/1.031052E-05","","","","","3a04c63c-6a59-4047-ad51-0125a7544dad"]
["18","拆卸齿箱连接器","拆卸齿箱连接器-18-拆除发电机与齿箱连接器固定螺栓","拆除发电机与齿箱连接器固定螺栓","使用开口扳手拆除发电机与齿箱连接器上的螺栓","","","","开口扳手","18","-3.003472/120.8115/-1.202358","46.7501/355.0503/9.656919E-06","","","","","b35a45ca-f586-4be2-ab8d-386229b0007b"]
["19","拆卸齿箱连接器","拆卸齿箱连接器-19-拆除发电机与齿箱连接器","拆除发电机与齿箱连接器","拆除发电机与齿箱连接器","","","","","19","-3.003472/120.8115/-1.202358","46.7501/355.0503/9.656919E-06","","","","","3ce7ba2c-89ef-422b-896e-5b3073f1cfc9"]
["20","拆卸发电机前端轴承","拆卸发电机前端轴承-20-拆除发电机法兰","拆除发电机法兰","拆除发电机前段法兰","","","","","20","-3.119088/120.6252/-1.030369","42.55009/325.9004/1.043044E-05","","","","","f55cb728-2c98-4f66-bb5e-4840d75d059c"]
["21","拆卸发电机前端轴承","拆卸发电机前端轴承-21-拆除发电机轴承前端压圈螺栓","拆除发电机轴承前端压圈螺栓","使用开口扳手拆除发电机轴承前端压圈螺栓","","","","开口扳手","21","-3.187941/120.4414/-0.8148926","40.60011/303.7006/1.124466E-05","","","","","da1a50f1-cbc1-4afd-a2a3-91b7d39c1d16"]
["22","拆卸发电机前端轴承","拆卸发电机前端轴承-22-拆除发电机轴承前端压圈","拆除发电机轴承前端压圈","拆除发电机轴承前端压圈","清除压圈上轴承溢出的润滑油，清理设备上的灰尘","","","","22","-3.187941/120.4414/-0.8148926","40.60012/303.7006/6.746797E-06","","","","","e9baf657-4cda-419c-b0ec-762dde6612e7"]
["23","拆卸发电机前端轴承","拆卸发电机前端轴承-23-拆除发电机轴承前端油封","拆除发电机轴承前端油封","拆除发电机轴承前端油封","清除油封上轴承溢出的润滑油，清理设备上的灰尘","","","一字螺丝刀","23","-3.187941/120.4414/-0.8148926","40.60012/303.7006/6.746797E-06","","","","","3e749bda-ccc8-472b-9c3a-5c3a1b86b46c"]
["24","拆卸发电机前端轴承","拆卸发电机前端轴承-26-拆除发电机输出端润滑油管及传感器","拆除发电机输出端润滑油管及传感器","轻轻拆除发电机输出端润滑油管及传感器","","","","","24","","","","","","",""]
["25","拆卸发电机前端轴承","拆卸发电机前端轴承-24-拆除发电机轴承前端盖螺栓","拆除发电机轴承前端盖螺栓","使用开口扳手拆除发电机轴承前端盖螺栓","","","","开口扳手","25","-3.187941/120.4414/-0.8148926","40.60012/303.7006/6.746797E-06","","","","","114d872d-47bc-4d1f-a6d7-4a0aa5ba24e6"]
["26","拆卸发电机前端轴承","拆卸发电机前端轴承-25-拆除发电机轴承前端盖","拆除发电机轴承前端盖","拆除发电机轴承前端盖","","","","","26","-2.950788/120.6845/-0.9724608","40.45012/303.6006/6.731716E-06","","","","","b18749aa-61f8-4d01-9c33-a5264ded7c10"]
["27","拆卸发电机前端轴承","拆卸发电机前端轴承-27-拆除发电机轴承前端甩油盘","拆除发电机轴承前端甩油盘","拆除发电机轴承前端甩油盘","清除甩油盘上轴承溢出的润滑油，清理设备上的灰尘","","","一字螺丝刀","27","-3.092992/120.5843/-0.8851638","37.50014/303.5507/6.456962E-06","","","","","c53a0812-85b3-4415-98f7-6f74f2acb5df"]
["28","拆卸发电机前端轴承","拆卸发电机前端轴承-28-拆除发电机轴承前盖螺栓","拆除发电机轴承前盖螺栓","使用开口扳手拆除发电机轴承前盖螺栓","","","","开口扳手","28","-3.092992/120.5843/-0.8851638","37.50014/303.5507/6.456962E-06","","","","","bfe262a2-6d68-44dc-a346-3b6507b7ea07"]
["29","拆卸发电机前端轴承","拆卸发电机前端轴承-29-拆除发电机前轴承套","拆除发电机前轴承套","拆除发电机前轴承套","","","","","29","-2.942086/120.7554/-0.9890749","43.05014/304.5507/7.010053E-06","","","","","fb6e461e-56a9-4cc0-ac66-9604c6e2e662"]
["30","拆卸发电机前端轴承","拆卸发电机前端轴承-30-拆除发电机输出端外壳螺栓","拆除发电机输出端外壳螺栓","使用开口扳手拆除发电机输出端外壳螺栓","","","","开口扳手","30","-2.732944/120.973/-1.132951","37.60014/303.9008/6.465629E-06","","","","","c66df05d-6497-43a3-97f9-2b4c955a9219"]
["31","拆卸发电机前端轴承","拆卸发电机前端轴承-31-拆除发电机输出端外壳","拆除发电机输出端外壳","拆除发电机输出端外壳","防止重物砸伤","","","","31","-2.732944/120.973/-1.132951","37.60014/303.9008/6.465629E-06","","","","","a1b6ed50-8f8e-43fe-a9e8-ad3cbd736a3c"]
["32","拆卸发电机前端轴承","拆卸发电机前端轴承-32-拆除发电机前轴承","拆除发电机前轴承","使用大功率热风枪加热轴承，对辅助线及传感器做隔热防护。温度控制在90摄氏度到100摄氏度，用轴承拉马器取出轴承","在发电机厂家技术人员指导下拆除，防止转子与定子之间发生刮蹭，防止人员烫伤，防止设备起火","","","热风枪","32","-3.071776/120.6586/-0.9052575","37.60014/303.9008/6.465629E-06","","","","","6ace1e93-aeeb-4a4f-a917-4093ac88373c"]
["33","发电机前端轴承更换","发电机前端轴承更换-33-清理转子油污","清理转子油污","使用百洁布清理转子上的油污","","","","百洁布","33","-3.071776/120.6586/-0.9052575","37.60014/303.9008/6.465629E-06","","","","","71efe30b-e5ac-4d5b-bd05-92654625da5f"]
["34","发电机前端轴承更换","发电机前端轴承更换-34-更换新轴承","更换新轴承","更换新轴承","在发电机厂家技术人员指导下安装新轴承，防止转子与定子之间发生刮蹭，防止人员烫伤，防止设备起火","","","热风枪","34","-2.197941/121.2777/-1.434059","42.40013/294.1009/4.624655E-06","","","","","93c5b784-cc95-4fc8-9720-8f26db88a004"]
["35","发电机前端轴承更换","发电机前端轴承更换-35-轴承加润滑油","轴承加润滑油","轴承按设计要求加注润滑油","","","","润滑脂","35","-3.071776/120.6586/-0.9052575","37.60014/303.9008/6.465629E-06","","","","","3fb25e1b-429a-491e-b81b-decfeef7cf60"]
["36","回装发电机前端轴承","回装发电机前端轴承-36-安装发电机输出端外壳螺栓","安装发电机输出端外壳螺栓","安装发电机输出端外壳","","","","","36","-2.522621/121.1684/-1.277074","37.55013/304.1008/4.307527E-06","","","","","30fe5bff-e874-4f4a-8fae-87738a9188eb"]
["37","回装发电机前端轴承","回装发电机前端轴承-37-安装发电机输出端外壳螺栓","安装发电机输出端外壳螺栓","安装发电机输出端外壳螺栓","防止重物砸伤","","","开口扳手","37","-2.522621/121.1684/-1.277074","37.55013/304.1008/4.307527E-06","","","","","0a3dc7e6-5803-4b44-9ff7-7c48792a3bc9"]
["38","回装发电机前端轴承","回装发电机前端轴承-38-安装发电机前轴承套","安装发电机前轴承套","安装发电机前轴承套","","","","","38","-2.999337/120.7198/-0.9542134","44.40014/304.2508/7.169837E-06","","","","","b2b44bf4-6f18-4947-9218-3e35a3535584"]
["39","回装发电机前端轴承","回装发电机前端轴承-39-安装发电机轴承前盖螺栓","安装发电机轴承前盖螺栓","安装开口扳手拆除发电机轴承前盖螺栓","","","","开口扳手","39","-2.999337/120.7198/-0.9542134","44.17878/304.3061/7.142867E-06","","","","","48549d8d-da2e-45b6-ad8e-0422362b24b3"]
["40","回装发电机前端轴承","回装发电机前端轴承-40-安装发电机轴承前端甩油盘","安装发电机轴承前端甩油盘","安装发电机轴承前端甩油盘","","","","一字螺丝刀","40","-2.999337/120.7198/-0.9542134","44.40014/304.2508/4.779893E-06","","","","","514a684d-5342-4a92-bf8e-283f55d1a412"]
["41","回装发电机前端轴承","回装发电机前端轴承-42-安装发电机轴承前端盖","安装发电机轴承前端盖","安装发电机轴承前端盖","","","","","41","-3.113055/120.6182/-0.8604507","45.25014/305.5012/7.276346E-06","","","","","52911f26-664b-4c22-bb6e-4afcc4a22621"]
["42","回装发电机前端轴承","回装发电机前端轴承-43-安装发电机轴承前端盖螺栓","轴承安装加热处理","安装发电机轴承前端盖螺栓","","","","开口扳手","42","-2.970438/120.3733/-0.9642273","26.25015/304.3511/5.711678E-06","","","","","218d1508-7d88-47a8-9bbd-8a09731b4de2"]
["43","回装发电机前端轴承","回装发电机前端轴承-41-安装发电机输出端润滑油管及传感器","安装发电机输出端润滑油管及传感器","安装发电机输出端润滑油管及传感器","","","","","43","","","","","","",""]
["44","回装发电机前端轴承","回装发电机前端轴承-44-安装发电机轴承前端油封","安装发电机轴承前端油封","安装发电机轴承前端油封","","","","一字螺丝刀","44","-2.970438/120.3733/-0.9642273","26.25015/304.3511/5.711678E-06","","","","","883ce4d5-8455-4566-82e3-12c8aeb556f6"]
["45","回装发电机前端轴承","回装发电机前端轴承-45-安装发电机轴承前端压圈","安装发电机轴承前端压圈","安装发电机轴承前端压圈","","","","","45","-2.970438/120.3733/-0.9642273","26.25015/304.3511/5.711678E-06","","","","","7b02318a-81a9-4f00-a31e-3e1fbb2770ab"]
["46","回装发电机前端轴承","回装发电机前端轴承-46-安装发电机轴承前端压圈螺栓","安装发电机轴承前端压圈螺栓","安装发电机轴承前端压圈螺栓","","","","开口扳手","46","-2.970438/120.3733/-0.9642273","26.25015/304.3511/5.711678E-06","","","","","c2c304c0-c0f5-4ed8-a685-d5adb13b0677"]
["47","回装发电机前端轴承","回装发电机前端轴承-47-安装发电机法兰","安装发电机法兰","安装发电机前段法兰","","","","","47","-2.898651/120.6467/-1.529418","26.90015/338.751/4.786819E-06","","","","","15c26b2a-610a-4dd9-9058-0a1389be5197"]
["48","拆除励磁滑滑环室","拆除励磁滑滑环室-48-拆除编码器保护壳螺栓","拆除编码器保护壳螺栓","使用开口扳手拆除编码器保护壳螺栓","","","","开口扳手","48","-7.329741/120.2594/-0.7513216","29.35013/46.50077/5.87701E-06","","","","","d4a0d30b-2ae6-4255-b60e-09a4315508ae"]
["49","拆除励磁滑滑环室","拆除励磁滑滑环室-49-拆除编码器保护壳","拆除编码器保护壳","拆除编码器保护壳","","","","","49","-7.329741/120.2594/-0.7513216","29.35013/46.50077/5.87701E-06","","","","","5eded7f5-6a27-4772-b9a4-dea62a5379df"]
["50","拆除励磁滑滑环室","拆除励磁滑滑环室-50-拆除编码器外壳","拆除编码器外壳","拆除编码器外壳","","","","","50","-7.329741/120.2594/-0.7513216","29.35013/46.50077/5.87701E-06","","","","","0158b057-acc4-43a1-9e79-b93965eef197"]
["51","拆除励磁滑滑环室","拆除励磁滑滑环室-51-拆除编码器接线","拆除编码器接线","拆除编码器接线","","","","","51","-7.533643/120.2712/-0.5708688","24.50013/97.50076/3.753014E-06","","","","","3f3109a6-30bb-4c8e-987f-d2cacca84038"]
["52","拆除励磁滑滑环室","拆除励磁滑滑环室-52-拆除编码器","拆除编码器","拆除编码器","","","","","52","-7.377425/120.2041/-0.5114757","22.20013/89.55078/4.610657E-06","","","","","ea9355c9-4f5b-433e-b2cc-bff4fc4fea90"]
["53","拆除励磁滑滑环室","拆除励磁滑滑环室-53-拆掉励磁滑环壳螺栓","拆掉励磁滑环壳螺栓","使用开口扳手拆掉励磁滑环壳螺栓","","","","开口扳手","53","-7.337479/120.1032/0.754081","13.50013/142.4009/5.268206E-06","","","","","e92b3d90-a6b5-4522-a8f9-1fe5d8f0647c"]
["54","拆除励磁滑滑环室","拆除励磁滑滑环室-54-拆掉励磁滑环壳","拆掉励磁滑环壳","拆掉励磁滑环壳","","","","","54","-7.337479/120.1032/0.754081","13.50013/142.4009/5.268206E-06","","","","","d707ab2a-5432-441a-86db-c6fde7d6145b"]
["55","拆除励磁滑滑环室","拆除励磁滑滑环室-55-拆除励磁滑环电缆连接线","拆除励磁滑环","拆除励磁滑环","先验电后放电","","","开口扳手","55","-6.676769/120.0092/0.9404251","6.500126/181.3009/5.531727E-06","","","","","3f85ce2f-4a93-4779-89a1-a36df0d234fd"]
["56","拆除励磁滑滑环室","拆除励磁滑滑环室-56-拆除励磁滑滑环室","拆除励磁滑滑环室","拆除励磁滑滑环室","","","","","56","-6.676769/120.0092/0.9404251","6.500126/181.3009/5.531727E-06","","","","","f21a85ff-6f89-4ad1-be89-1e355a971feb"]
["57","拆除发电机后端轴承","拆除发电机后端轴承-57-拆除发电机轴承后端压圈螺栓","拆除发电机轴承后端压圈螺栓","使用开口扳手拆除发电机轴承后端压圈螺栓","","","","开口扳手","57","-6.734606/119.9116/-0.006630383","6.000123/133.4508/5.580097E-06","","","","","a61ae328-c33d-4f9d-941d-4b6569e2011c"]
["58","拆除发电机后端轴承","拆除发电机后端轴承-58-拆除发电机轴承后端压圈","拆除发电机轴承后端压圈","拆除发电机轴承后端压圈","清除压圈上轴承溢出的润滑油，清理设备上的灰尘","","","","58","-6.734606/119.9116/-0.006630361","6.000124/133.4508/6.009336E-06","","","","","f4e097e4-193b-4718-a556-16369931cd74"]
["59","拆除发电机后端轴承","拆除发电机后端轴承-59-拆除发电机轴承后端油封","拆除发电机轴承后端油封","拆除发电机轴承后端油封","清除油封上轴承溢出的润滑油，清理设备上的灰尘","","","一字螺丝刀","59","-6.647587/120.0619/-0.07652974","18.60012/128.0508/6.30578E-06","","","","","d42f5238-2a5c-4aa4-bc35-3c326748230e"]
["60","拆除发电机后端轴承","拆除发电机后端轴承-62-拆除发电机后端润滑油管及传感器","拆除发电机后端润滑油管及传感器","轻轻拆除发电机后端润滑油管及传感器","","","","","60","-7.462842/120.3919/0.5666389","16.95012/128.4009/5.355281E-06","","","","","1392e5c4-3d07-4f0f-86d0-e1dd18fbd846"]
["61","拆除发电机后端轴承","拆除发电机后端轴承-60-拆除发电机轴承后端盖螺栓","拆除发电机轴承后端盖螺栓","使用开口扳手拆除发电机轴承后端盖螺栓","","","","开口扳手","61","-6.647587/120.0619/-0.07652974","18.60012/128.0508/6.30578E-06","","","","","2b961400-508e-4724-9389-059936d847bc"]
["62","拆除发电机后端轴承","拆除发电机后端轴承-61-拆除发电机轴承后端盖","拆除发电机轴承后端盖","拆除发电机轴承后端盖","","","","","62","-7.051151/120.2578/0.2532654","21.00012/129.4509/5.487096E-06","","","","","e80afbf7-3c01-4022-a581-cd20efc9b11e"]
["63","拆除发电机后端轴承","拆除发电机后端轴承-63-拆除发电机轴承后端甩油盘","拆除发电机轴承后端甩油盘","拆除发电机轴承后端甩油盘","清除甩油盘上轴承溢出的润滑油，清理设备上的灰尘","","","一字螺丝刀","63","-6.834918/120.1477/0.06893648","16.95012/128.4009/5.801553E-06","","","","","1bf35c1f-df1c-4966-a665-c6f76236ea36"]
["64","拆除发电机后端轴承","拆除发电机后端轴承-64-拆除发电机轴承后盖螺栓","拆除发电机轴承后盖螺栓","使用开口扳手拆除发电机轴承后盖螺栓","","","","开口扳手","64","-6.834918/120.1477/0.06893648","16.95012/128.4009/5.801553E-06","","","","","f9a817fa-cd79-4180-87d8-a8d097b819ab"]
["65","拆除发电机后端轴承","拆除发电机后端轴承-65-拆除发电机后轴承套","拆除发电机后轴承套","拆除发电机后轴承套","","","","","65","-6.834259/120.1481/0.06841277","16.90012/128.4009/6.246169E-06","","","","","b3d4b982-5495-4a23-80ea-915e0613b511"]
["66","拆除发电机后端轴承","拆除发电机后端轴承-66-拆除发电机后端外壳螺栓","拆除发电机后端外壳螺栓","使用开口扳手拆除发电机后端外壳螺栓","","","","开口扳手","66","-7.415746/120.3735/0.529308","16.90012/128.4009/8.476944E-06","","","","","9e930cc4-8e16-467a-8f21-e31604b1c8c9"]
["67","拆除发电机后端轴承","拆除发电机后端轴承-67-拆除发电机后端外壳","拆除发电机后端外壳","拆除发电机后端外壳","防止重物砸伤","","","","67","-7.415746/120.3735/0.529308","16.90012/128.4009/8.476944E-06","","","","","b5695f0f-867a-4cb3-aa78-bc8e4000f577"]
["68","拆除发电机后端轴承","拆除发电机后端轴承-68-拆除发电机后轴承","拆除发电机后轴承","使用大功率热风枪加热轴承，对辅助线及传感器做隔热防护。温度控制在90摄氏度到100摄氏度，用轴承拉马器取出轴承","在发电机厂家技术人员指导下拆除，防止转子与定子之间发生刮蹭，防止人员烫伤，防止设备起火","","","热风枪","68","-6.78316/120.1283/0.02790905","16.90012/128.4009/8.476944E-06","","","","","4fbe53fe-ee96-4b4e-8159-596c0e812c61"]
["69","发电机后端轴承更换","发电机后端轴承更换-69-清理转子油污","清理转子油污","使用百洁布清理转子上的油污","","","","百洁布","69","-6.78316/120.1283/0.02790905","16.90012/128.4009/8.476944E-06","","","","","a190cf20-b4d8-4fa7-aad4-e4a353c15a9e"]
["70","发电机后端轴承更换","发电机后端轴承更换-70-更换新轴承","更换新轴承","更换新轴承","在发电机厂家技术人员指导下安装新轴承，防止转子与定子之间发生刮蹭，防止人员烫伤，防止设备起火","","","热风枪","70","-7.761213/120.2466/0.6981454","18.90012/123.6508/9.926713E-06","","","","","f590056e-d196-45c6-b5cd-3db81bf5b54a"]
["71","发电机后端轴承更换","发电机后端轴承更换-71-轴承加润滑油","轴承加润滑油","给轴承按设计要求加注润滑油","","","","润滑脂","71","-6.78316/120.1283/0.02790905","16.90012/128.4009/8.476944E-06","","","","","9aaee223-2cb9-4543-a744-c9f6c4b5b8f7"]
["72","回装发电机后端轴承","回装发电机后端轴承-72-安装发电机后端外壳","安装发电机后端外壳","安装发电机后端外壳","防止重物砸伤","","","","72","-7.580572/120.4374/0.6599501","16.90012/128.4009/8.476944E-06","","","","","8fc60b52-8052-490f-834f-33dade1cbdaa"]
["73","回装发电机后端轴承","回装发电机后端轴承-73-安装发电机后端外壳螺栓","安装发电机后端外壳螺栓","使用开口扳手安装发电机后端外壳螺栓","","","","开口扳手","73","-7.580572/120.4374/0.6599501","16.90012/128.4009/8.476944E-06","","","","","9b3be08f-a3f4-415e-8379-a24e20e05715"]
["74","回装发电机后端轴承","回装发电机后端轴承-74-安装发电机后轴承套","安装发电机后轴承套","安装发电机后轴承套","","","","","74","-6.921533/120.1827/0.1375851","16.85012/128.4009/8.028662E-06","","","","","d36e1a53-164c-4d96-ad5d-a75cbe3fdbd5"]
["75","回装发电机后端轴承","回装发电机后端轴承-75-安装发电机轴承后盖螺栓","安装发电机轴承后盖螺栓","安装发电机轴承后盖螺栓","","","","开口扳手","75","-6.921533/120.1827/0.1375851","16.85012/128.4009/8.028662E-06","","","","","c47a887c-269d-4e96-9fe8-e271d8ca6e7e"]
["76","回装发电机后端轴承","回装发电机后端轴承-76-安装发电机轴承后端甩油盘","安装发电机轴承后端甩油盘","安装发电机轴承后端甩油盘","","","","一字螺丝刀","76","-6.921533/120.1827/0.1375851","16.85012/128.4009/8.028662E-06","","","","","1ccdf222-1778-4fab-a127-06be10c0ba36"]
["77","回装发电机后端轴承","回装发电机后端轴承-78-安装发电机轴承后后端盖","安装发电机轴承后端盖","安装发电机轴承后端盖","","","","","77","-7.076949/120.2428/0.2607689","16.85012/128.4009/8.028662E-06","","","","","104a37ee-64ee-4915-8663-7ad6963b0e9c"]
["78","回装发电机后端轴承","回装发电机后端轴承-79-安装发电机轴承后端盖螺栓","安装发电机轴承后端盖螺栓","安装发电机轴承后端盖螺栓","","","","开口扳手","78","-6.717388/120.0984/-0.02793042","19.05013/129.9009/7.225927E-06","","","","","af884097-db71-4778-b97e-1166430e8fd3"]
["79","回装发电机后端轴承","回装发电机后端轴承-77-安装发电机后端润滑油管及传感器","安装发电机后端润滑油管及传感器","安装发电机后端润滑油管及传感器","","","","","79","-7.486093/120.4009/0.5850637","16.85012/128.4009/8.028662E-06","","","","","ebc829a3-3051-4fb4-b0fe-ec950d2cbf5e"]
["80","回装发电机后端轴承","回装发电机后端轴承-80-安装发电机轴承后端油封","安装发电机轴承后端油封","安装发电机轴承后端油封","","","","一字螺丝刀","80","-6.717388/120.0984/-0.02793042","19.05013/129.9009/7.225927E-06","","","","","027650f4-cef2-44f7-a678-a2f0f9ff8d3e"]
["81","回装发电机后端轴承","回装发电机后端轴承-81-安装发电机轴承后端压圈","安装发电机轴承后端压圈","安装发电机轴承后端压圈","","","","","81","-6.717388/120.0984/-0.02793042","19.05013/129.9009/7.225927E-06","","","","","2dde275b-7333-4efa-8ab1-3d85e87f22aa"]
["82","回装发电机后端轴承","回装发电机后端轴承-82-安装发电机轴承后端压圈螺栓","安装发电机轴承后端压圈螺栓","使用开口扳手安装发电机轴承后端压圈螺栓","","","","开口扳手","82","-6.717388/120.0984/-0.02793042","19.05013/129.9009/7.225927E-06","","","","","89724c02-eb18-4c5f-9deb-a8cc13b20df7"]
["83","回装励磁滑滑环室","回装励磁滑滑环室-83-安装励磁滑滑环室","安装励磁滑滑环室","安装励磁滑滑环室","","","","","83","-6.50842/120.2773/0.8648475","21.65013/183.7509/7.980123E-06","","","","","f01d0054-f48a-4a6c-bcf0-56843ca3a7f4"]
["84","回装励磁滑滑环室","回装励磁滑滑环室-84-安装励磁滑环电缆连接线","安装励磁滑环电缆连接线","安装励磁滑环","","","","开口扳手","84","-6.50842/120.2773/0.8648475","21.65013/183.7509/7.980123E-06","","","","","f2b2e09e-29fa-434b-85ce-dd0b13752cb9"]
["85","回装励磁滑滑环室","回装励磁滑滑环室-85-安装励磁滑环壳","安装励磁滑环壳","安装励磁滑环壳","","","","","85","-6.50842/120.2773/0.8648475","21.65013/183.7509/7.980123E-06","","","","","a8b8e9aa-056c-41da-bbd8-1e7ab3110775"]
["86","回装励磁滑滑环室","回装励磁滑滑环室-86-安装励磁滑环壳螺栓","安装励磁滑环壳螺栓","使用开口扳手安装励磁滑环壳螺栓","","","","开口扳手","86","-6.50842/120.2773/0.8648475","21.65013/183.7509/7.980123E-06","","","","","186c2a2c-bcda-4455-959b-0a9aba655e82"]
["87","回装励磁滑滑环室","回装励磁滑滑环室-87-安装编码器","安装编码器","安装编码器","","","","","87","-7.412585/120.1605/-0.4496454","10.75012/95.10081/8.255738E-06","","","","","65d13a15-2070-48e5-8492-6abacb55623f"]
["88","回装励磁滑滑环室","回装励磁滑滑环室-88-安装编码器接线","安装编码器接线","安装编码器接线","","","","","88","-7.580649/120.1907/-0.5496108","10.95012/98.85081/8.261263E-06","","","","","a9039c84-5a3d-45a5-8725-8e61a0db5081"]
["89","回装励磁滑滑环室","回装励磁滑滑环室-89-安装编码器外壳","安装编码器外壳","安装编码器外壳","","","","","89","-7.516737/120.1786/-0.4889262","11.50012/87.40083/8.712648E-06","","","","","492ec516-3487-40f8-b970-c663fafc66c0"]
["90","回装励磁滑滑环室","回装励磁滑滑环室-90-安装编码器保护壳","安装编码器保护壳","安装编码器保护壳","","","","","90","-7.400027/120.1649/-0.287481","13.50012/122.0009/8.780342E-06","","","","","4966aa39-ecb4-4670-95fe-e11112d99562"]
["91","回装励磁滑滑环室","回装励磁滑滑环室-91-安装编码器保护壳螺栓","安装编码器保护壳螺栓","使用开口扳手安装编码器保护壳螺栓","","","","开口扳手","91","-7.400027/120.1649/-0.287481","13.50012/122.0009/8.780342E-06","","","","","3e3bf1b0-2a55-4b20-91e4-b5ee445e7746"]
["92","回装联轴器","回装联轴器-92-发电机做绝缘测试","发电机做绝缘测试","定子，转子做绝缘测试","","","","绝缘摇表","92","-2.903524/121.3705/1.406158","32.60009/219.8009/9.120955E-06","","","","","ec7c861c-9c8c-4aca-a596-6ee1e9e67e09"]
["93","回装联轴器","回装联轴器-93-运行前检查","运行前检查","盘车转到检查发电机是否有异响，卡顿","","","","","93","-2.696035/121.3364/1.657859","22.6001/219.3509/9.71028E-06","","","","","62ae92d7-b77f-4a7c-96fb-afe21ba50840"]
["94","回装联轴器","回装联轴器-96-安装联轴器","安装联轴器","安装联轴器","","","","","94","-3.084546/120.8337/0.2096501","42.65008/183.8008/1.001189E-05","","","","","10ed9c46-8416-4d4b-95b1-7f335dbad6b1"]
["95","回装联轴器","回装联轴器-97-安装联轴器螺栓","安装联轴器螺栓","安装联轴器螺栓","","","","","95","-3.084546/120.8337/0.2096501","42.65008/183.8008/1.001189E-05","","","","","b1ad6ba0-4108-4e59-bad0-88b34b2b2b3d"]
["96","回装联轴器","回装联轴器-94-发电电机做对中","发电电机做对中","发电电机做对中","","","","","96","-2.696035/121.3364/1.657859","22.6001/219.3509/9.71028E-06","","","","","3b0b2836-2c34-4481-8599-bd9785b67371"]
["97","回装联轴器","回装联轴器-95-复位部件并激光对中","复位部件并激光对中","复位核心部件并激光对中","必须发电机厂家技术人员指导下操作，防止重物砸伤","","","","97","-2.696035/121.3364/1.657859","22.6001/219.3509/9.71028E-06","","","","","1909f217-2de2-47f4-8e85-3e366746c11e"]
["98","回装联轴器","回装联轴器-97-安装联轴器螺栓","安装联轴器螺栓","安装联轴器螺栓","","","","","98","-3.084546/120.8337/0.2096501","42.65008/183.8008/1.001189E-05","","","","","b1ad6ba0-4108-4e59-bad0-88b34b2b2b3d"]
["99","部件调试","部件调试-98-紧固高强度连接螺栓","紧固高强度连接螺栓","按既定顺序和力矩分步紧固高强度连接螺栓。操作员与检查员请同步确认。","必须使用液压拉伸器，双人复核，确保力矩准确。","","","","99","-2.789742/121.4872/1.499427","26.20008/221.3508/9.515366E-06","","","","","a2f351f8-36a7-4a93-8532-3ea98fd3c2c0"]
["100","部件调试","部件调试-100-检查各部件均安装完毕各连接处密封性良好","检查各部件均安装完毕各连接处密封性良好","检查各部件均安装完毕各连接处密封性良好","","","","","100","-2.789742/121.4872/1.499427","26.20008/221.3508/9.515366E-06","","","","","41118a47-ffab-4653-933a-db4521f9a8a2"]
["101","部件调试","部件调试-101-恢复所有连接","恢复所有连接","联轴器、所有线缆与管路已恢复连接，经检查确认牢固、无泄漏。","逐项检查，确保电气连接正确，管路无泄漏。","","","","101","-2.789742/121.4872/1.499427","26.20008/221.3508/9.515366E-06","","","","","e38b551c-acf0-4aec-817e-9e52c5c3e2c8"]
["102","部件调试","部件调试-102-加注新润滑脂","加注新润滑脂","润滑脂加注设备与油脂牌号确认无误，现在开始定量加注。","确保润滑脂清洁，并准确记录加注量。","","","","102","-4.057802/120.7268/-2.139572","24.20008/337.1009/9.828342E-06","","","","","c88d5204-9332-4887-8ce8-b7e94892565c"]
["103","部件调试","部件调试-103-螺栓紧固","螺栓紧固","紧固各部位螺栓，力矩达到厂家规定值。","","","","力矩扳手","103","-2.717255/122/-1.866121","35.85008/316.2511/8.426587E-06","","","","","9f0d6e0f-ad86-438b-afd9-0b37a6708b1b"]
["104","部件调试","部件调试-104-打开润滑油供油装置","打开润滑油供油装置","打开润滑油供油装置","","","","","104","-4.492351/120.4533/-2.16241","10.55004/358.5013/8.426723E-06","","","","","b8e8f484-050c-49c7-bbec-af4b2b3abe9c"]
["105","部件调试","部件调试-105-安装发电机与齿箱连接器保护罩","安装发电机与齿箱连接器保护罩","使用开口扳手安装发电机与齿箱连接器保护罩","","","","开口扳手","105","-3.146373/121.143/-1.499323","39.65004/357.9016/8.455057E-06","","","","","6174178e-ff89-440b-96dd-a8cc5d334d06"]
["106","最终测试","最终测试-106-最终清场与现场恢复","最终清场与现场恢复","所有工具已清点，机舱内无任何遗留物，机舱罩已安装，进行最终检查。","","","","","106","-2.38858/122/1.798682","39.55007/227.1514/6.643562E-06","","","","","64c851d7-972d-4fac-a305-b4b1b6d5bcfb"]
["107","最终测试","最终测试-107-解除安全锁定","解除安全锁定","所有作业项目完成，解除安全锁，恢复供电。","必须由执行上锁的人员亲自解锁","","","","107","-2.38858/122/1.798682","39.55007/227.1514/6.643562E-06","","","","","de5f33a7-393e-41ef-9a86-ab15a82f6179"]
["108","最终测试","最终测试-108-试运行与数据监测","试运行与数据监测","风机已启动，空转正常。开始逐级加载，监控室持续关注轴承温度与振动数据。","任何异常需立即通报停机","","","","108","-2.38858/122/1.798681","39.55009/227.1514/5.536304E-06","","","","","73398c75-93a5-4a5c-8351-b03ceed54e4b"]
["109","结尾工作","结尾工作-110-工作终结","工作终结","工作终结，清理现场","","","","","109","-2.38858/122/1.798681","39.55009/227.1514/5.536304E-06","","","","","89a449d3-ada0-4961-8a2e-1b7f0f9ce04a"]